Scope of Accreditation for the Testing Laboratory (Center)

Testing Center of High-voltage Equipment

Joint Stock Company «Research and Development Center at Federal Grid Company of Unified Energy System», № RA.RU.21МВ06

Testing Laboratory (Testing Center) Name

127566, Moscow, Vysokovoltny proezd, 13

Business Address

| No. | Documents establishing rules and techniques of research (testing) and measurements | Equipment | OKPD 2 code | TN VED EAEU code | Defined parameter | Range |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 |
| 1. | GOST R 54827 Section 25 | Power transformers | 27.11.4 | 8504 210000 8504 220000 8504 230000 | Short-time withstand tests and current striking shocks (up to 40 MVA; up to 70 kА; 50 Hz) | Compliant / noncompliant |
| 2. | GOST 14794 § 6.12 | Reactors, including current-limiting reactors | 27.11.4 | 8504 | Short-time withstand tests (up to 40 kА; up to 0,56 Ω; 50 Hz) | Compliant / noncompliant |
| 3. | GOST R 52565 §§ 9.2.6; GOST 687 § 7.2.6; | AC current circuit-breakers for voltage 3 to 750 kV | 27.12.10.110 | 8535 210000 8535 290000 | Tests for mechanical capability during collective action of wires heaviness and wind load (0..10000) N | Compliant / noncompliant |
| 4. | GOST R 52726 § 8.5.6 | AC current disconnectors and earthing switches for voltage above 1 kV | 27.12.10.120 | 8535 300000 | Operation during application of rated static mechanical load to terminals (0..10000) N | Compliant / noncompliant |
| 5. | GOST R 52725-2007 § 9.20 | Non-linear surge arresters, Surge arresters with spark gaps | 27.12.10.130 | 8535 400000 | Tests for safety requirements (от 0 up to 1 Ω; от 0 up to 300 mm) | Compliant / noncompliant |
| 6 | GOST R 54828 § 5.18, 6.16, Annex G; | Metal-enclosed switchgears with SF6 insulation (GIS) | 27.12.10.190 | 8537 200000 | Tests for exposure of electric arc (localization capability): 63 kА up to 0,3 s | Compliant / noncompliant |
| 7. | IEC 60353 Section 9 | High-frequency line traps | 27.12.10.190 | 8535 900000 | Short-time withstand tests (up to 40 kА, with inductance up to 1,0 mH) | Compliant / noncompliant |
| 8. | GOST IEC 61439-6 § 10.2.3.1, 10.2.102, 10.10 | Busducts magistral and distributive | 27.32.13.199 | 8544 | Requirements to temperature rise and over-load currents: up to 12 kА up to 300 °С up to 1000 sequences | Passed / failed |
|  | GOST IEC 61439-6 § 10.5.2, 10.5.3, 10.11 |  |  |  | Requirements to short-time withstand tests: Ith = 125 kА Idyn=320 kА | Passed / failed |
| 9 | GOST 10693-81 § 6.12; GOST R 55187-2012 § 9,19; GOST R 52565-2006 § 9.2.6; | Sealed bushings | 27.90.12.120 | 8546 900000 | Mechanical wearing tests and cantilever loads tests (0..10000) N | Compliant / noncompliant |
| 10. | GOST ISO 6330 | Materials and special clothing for protection: - against thermal risks of electric arc; - against non-ionizing emissions; - against shock of electric current; - against exposures of static electricity; - against mechanical exposures; - against general industrial pollutions; - against heat and flame; - against high temperatures, low temperatures and heat emissions; - others. | 13.2 13.9 14.12 14.13 14.14 14.19 14.3 14.31 14.39 | 5208 5209 5210 5211 5515130000 5515220000 5516240000 5512 5513 5514 5515 5516 6201 6201139000 6202139000 6203291100 6203221000 6203228000 6203231000 6204231000 6211490000 6211390000 | Performing of washing and drying: up to 1000 cycles | Performed / not performed |

Deputy General Director of Exploitation,

Head of Testing Center

Joint Stock Company «Research and Development Center

at Federal Grid Company of Unified Energy System»												V.V. Boykov

Stamp